## Original
Envelope Air Leakage Testing Procedure |  | Shaded boxes will autofill.
Name Address |  | Project Name & Address |  | Testing should not be performed if:
| m-d-y | Date of Testing |  | D Temp Difference X Height > 1180
|  | Test Participants |  | Example, 30 oF x 40' = 1,200 (so do not test)
| ft2 | Building Conditioned Floor Area |  | If Building Baseline Pressure exceeds +/- 5 Pa,
| ft2 | Building Shell Area (SFBE) |  | then adjust pressure testing interval (*see below)
| oF | Outdoor Temperature at Start | D Temperature Difference |  | Building Height |  | Okay to test?
| oF | Indoor Temperature at Start |  | oF |  | ft
| ft | Elevation of project
Use data collection forms to capture basic description of building (e.g., type of occupancy, number of stories, wall, roof and foundation assembly type, orientation, etc.)
All designated team members perform set-up as assigned. Apply masking to all Outside Air (OA), Make-Up Air (MUA), and Exhaust and Dryers (Exh) fans but do not seal flue penetrations.
| Pa | Perform Pre Depressurization Baseline for 2 minutes (all fans covered)
| cfm | Depressurize building to -75 Pa and record single point result. *If Building Baseline pressure exceeds +/- 5 Pa, adjust range of test pressures. [Example, if Baseline is -10Pa, then test at -85Pa]
During single point testing, team should check for leaks in designated areas while BD's are operating. Document discovered leaks and/or building issues. Perform zone pressure testing, if applicable.
USACE Depressurization Multipoint Test
Continue depressurization from -75 Pa to -20Pa, adjusting fans for every 5 Pa interval*
*If Building Baseline pressure exceeds +/- 5 Pa, adjust range of test pressures. [Example, if Baseline is -10Pa, then test from -85 to -30 Pa]
| Pa | After -20 Pa (last data point) is recorded, cover all fans and perform post-baseline for 120 seconds
| cfm75 | Enter multipoint Depressurization curve fit value @ -75 Pa) - [Curve fit data shall have an R^2 > 0.98 for valid test]
| cfm50 | Enter multipoint Depressurization curve fit value @ -50 Pa) - [Curve fit data shall have an R^2 > 0.98 for valid test]
| sq. ft. | Approximate s.f. of equivalent opening
Reverse fans and add fan pressure reference tube(s).
| cfm75 | Perform Pressurization to single point @ +75 Pa
USACE Pressurization - With fans covered, perform pre- pressurization baseline for 120 secs
During pressurization testing, Fog machine leak identification can be performed
| cfm75 | USACE Pressurization (enter multipoint curve fit value @ +75 Pa)
The building pressure will be ramped down every 5 Pa interval. After +20 Pa is recorded, cover all fans and perform post-baseline for 120 seconds.
| cfm75 | With fans kept in pressurization mode, remove mask from OA (and hood MUA, if applicable). Record single point test value @ +75Pa
| cfm75 | Turn fans around and setup for depressurization mode (OA+MUA unmasked). Record single point test value @ -75Pa
| cfm75 | Keep fans in the same configuration (depressurization mode). Remove mask from exhaust fans. Record single point test value @ -75Pa
Cover all BD fans and keep all fans off. Remove mask from kitchen hood (if applicable).
| Pa | Record building baseline pressure for two 30 second periods
| Pa | Turn on all air handlers. Record building pressure for two 30 second periods
| Pa | With air handlers running, turn on all exhaust fans. Record building pressure for two 30 second periods
| Pa | If a kitchen hood is present, turn it on. With air handlers + all exhaust fans + hood on, record building pressure for two 30 second periods
| Pa | Record building baseline pressure for two 30 second periods
| oF | Outdoor Temperature at Finish
| oF | Indoor Temperature at Finish
Description of weather conditions during testing
Miscellaneous Notes