## Overview
Created using industry procedures*, this combustion appliance assessment tool is intended to help an assessor: - perform calculations and testing associated with combustion equipment, and - determine the relative safeness of the installed combustion equipment with respect to the building occupants' breathing zone. The workbook consists of 5 pages that walk the user through the assessment process as described below. When used on a tablet or laptop computer, the workbook will auto-populate the shaded fields based on user inputs in the non-shaded fields. To modify a programmed calculation or field function, simply unlock the sheet on the file tab; no passwords are used in this workbook in order to allow the user to modify the tool as they see fit. Users of this workbook are encouraged to review Southface's Small Commercial Combustion Appliance Guidelines and the referenced industry procedures* before performing combustion appliance assessments in the field.
Overview of tabs:
Page 1 | Enter basic information about the building type, combustion appliances and testing conditions.
Enter major gas leakage and CO levels encountered throughout the building.
Visually assess the Combustion Appliance Zone (CAZ).
Determine the total equipment input rating (kBtu/hr).
Page 2 | Assess the means of supplying combustion air to the appliances and determine whether combustion air is:
A) Supplied directly from outside? If so, are ducting and grill areas adequate?
B) Provided by the volume of space around the appliance (Unconfined Space) OR,
C) Provided by connection to a large interior volume space (Confined CAZ with Interior Connections)?
[Note: Strong preference is for all combustion air to come directly from the exterior, fully separating occupant breathing air from appliance combustion air. While neither approach B or C is recommended, the intent of the assessment is to determine if the installation complies with minimum code.]
Determine whether combustion air is adequate for the appliance based on code requirements and industry best practice.
Page 3 | Visually assess the installed appliance when it is not firing.
Visually assess the installed appliance when it is firing.
Page 4 | Perform CAZ worst case depressurization test.
Determine the magnitude of induced building pressures and how they could impact combustion safety.
Page 5 | Measure undiluted Carbon Monoxide (CO) in the flue.
Determine air-free CO levels and compare to industry thresholds.
Return building to original condition.
*References:
ACCA/RESNET (Standard 12), ANSI/BPI (1200-S-2015), National Fire Protection Agency (NFPA 54, ANSI Z223.1), International Building Code, International Fuel Gas Code, and International Residential Code

## Page 1
Small Commercial Combustion Appliance Assessment Workbook
| Project Name: | [6 empty] | Assessment Date:
| Project Address: | [6 empty] | Assessment Participants:
Building Description (e.g., type of occupancy, # of stories, wall, roof and foundation assembly type, orientation, etc.):
|  | ft2 | Building Conditioned Floor Area |  |  | Tools & Equipment Needed:
|  | ° F | Outdoor Temperature |  |  | ∙ Gas Leak Detector
|  | ° F | Indoor Temperature |  |  | ∙ Ambient CO Detector
|  | ° F | Δ T | Δ T = (Outdoor - Indoor) |  | ∙ Pressure Gauge & Tubing
∙ Combusiton Spillage Indicator
∙ Smoke Stick, mirror, etc.
∙ Probe-Type Combustion Analyzer (Optional)
Major Gas Leakage & Ambient Carbon Monoxide Detection:
|  | y / n | (1) Was smell of gas leakage noted in or around the building?
(2) Turn ON & Calibrate ambient CO detector outside, away from potential polluntant sources.
(3) Record ambient CO levels throughout the building:
|  | ppm | - ambient CO upon entering
|  | ppm | - ambient CO - describe location:
|  | ppm | - ambient CO - describe location:
|  | ppm | - ambient CO - describe location:
|  | ppm | - ambient CO upon entering the CAZ
→ |  |  | (4) Determine whether acceptable level of CO; appliance testing should not be performed if:
- Indoor ambient CO levels exceed 25 ppm
- Indoor ambient CO levels exceed 9 ppm for 15 minutes
Combustion Appliance Zone (CAZ) Visual Assessment:
|  | y / n | (1) Are atmospherically vented (category 1) combustion appliances installed?
(2) Appliances that are not sealed-combustion and direct venting should be installed in a zone or room that:
- can be sealed from the indoor space
- is connected to the outdoor space through wall openings or ducts
|  |  | (3) Is the CAZ a(n): | [5 empty] | Further describe the CAZ:
|  | y / n | - Mechanical closet that opens or vents to the outdoors?
|  | y / n | - Mechanical closet that opens or vents to the indoors?
|  | y / n | - Separate room that opens to the outdoors?
|  | y / n | - Separate room that opens to the indoors?
|  | y / n | - Unconditioned attic, basement, crawlspace, garage, etc.?
(4) Assess for deficiencies:
|  | y / n | - Visible Cracks, Gaps, or Openings in the boundaries between the CAZ and occupied space that prevent air-tight separation?
|  | y / n | - Are ducts and air handling unit (AHU) cabinets effectively sealed to prevent CAZ air movement into the living space?
|  | y / n | - Are exhaust devices present in the CAZ? (e.g., clothes dryers, exhaust fans, fireplaces, etc.)
Determine Total k-Btu/hr Rating of Appliances in the CAZ (Used to Calculate Required Air Volume of CAZ)
[5 empty] | model #s |  | Vented Appliance Categories as Defined by NFPA 54
|  | kBtu/hr | Water Heater 1 |  |  |  | Category 1 - operates with a nonpositive vent static pressure with a vent gas temp. that avoides excessive condensate production in the vent.
|  | kBtu/hr | Water Heater 2
|  | kBtu/hr | Furnace 1
|  | kBtu/hr | Furnace 2 |  |  |  | Category 2 - operates with a nonpositive vent static pressure and with a vent gas temp. that can cause excessive condensate production in the vent.
|  | kBtu/hr | Furnace 3
|  | kBtu/hr | other gas appliance
Category 3 - operates with a positive vent static pressure and with a vent gas temp. that avoids excessive condensate production in the vent.
→ |  |  | Total kBtu/hr
→ |  |  | ft3 | Required Volume of CAZ |  |  | Category 4 - Operates with a positive vent static pressure and with a vent gas temp that can cause excessive condensate production in the vent.
Volume = total kBtu/hr x 50

## Page 2
Net Free Area Multipliers: (fully blocked is 0, fully open is 1)
→ |  |  | Total kBtu/hr |  |  | - Assume that wood grilles or louvers have 25% net free area (0.25)
- Assume metal grilles or louvers have 75% net free area (0.75)
→ |  |  | ft3 | Required Volume of CAZ |  | - Prescribe increasing the size of the opening to meet the
minimum calculated net free area needed!
Assessment of Combustion (dilution) Air:
|  | y / n | (1) Is combusion air only provided via a direct ducted connection between the appliance and outdoors? (Strongly Recommended)
NOTE: if combustion air is provided to the CAZ via connection to interior spaces, skip down to Assessment of CAZ Volume
(2) Combustion air is provided to the CAZ from outdoors or a well ventilated space (e.g., attic) via:
|  | y / n | - Two Vertical Hi-Low Ducts (no horizontal runs)
|  | y / n | - Two Horizontal Hi-Low Ducts
|  | y / n | - Single Opening
|  |  | (3) Calculate Net Free Area of Air Ducts (Round/Rectangular) |  |  |  | Net Free Area Codes:
|  | in | - Diameter of each round duct |  |  |  | ∙ vertical ducts: | 1 in2 for 4 kBtu/hr
|  |  | - Net free area multiplier for round duct (between 0 and 1) |  |  |  | ∙ horizontal ducts: | 1 in2 for 2 kBtu/hr
|  | in2 | - Calculated cross sectional area of each round duct |  |  |  | ∙ single duct: | 1 in2 for 3 kBtu/hr
|  | in | - Length of opening of Rectangular duct
|  | in | - Width of opening of Rectangular duct
- Net free area multiplier for rectangular duct (between 0 and 1)
|  | in2 | - Calculated net free area for rectangular duct
|  | in2 | TOTAL (round + rectangular) net free cross sectional area of each installed connecting duct (Hi or Low)
|  | in2 | CALCULATED cross sectional net free area required by code for each duct
(4) Check ducts and answer as appropriate:
|  | y / n | - do the Two Hi-Low ducts terminate within 1' of ceiling and 1' of floor?
|  | y / n | - is the Single duct opening a minimum of 3" in both horizontal and vertical dimension?
→ |  |  |  | Undersized or Adequate? Is the duct area greater or less than the net free area needed?
BEST PRACTICE DICTATES:
∙ ALL combustion air should come from the outdoor space
∙ Do NOT use combustion air from the inside space
∙ Do NOT accept a hybrid approach (mix of inside and outdoor air)
Assessment of CAZ Volume:
|  | y/n | (1) Is combustion air provided via indoor volume of CAZ or connection with occupied space? (NOT RECOMMENDED!)
(2) Determine the total volume of the CAZ
|  | ft | - length, CAZ
|  | ft | - width, CAZ
|  | ft | - height, CAZ
|  | ft3 | - volume, CAZ |  | Volume = length x width x height
→ |  |  | ft3 | Required Volume of CAZ
→ |  |  |  | Confined or Unconfined? Is the volume of the CAZ greater or less than the volume required for minimum code?
(3) Determine the total volume of the connected spaces
|  | ft | - length, space connected to CAZ |  |  | ∙ Connected Space shall not have closeable interior
|  | ft | - width, space connected to CAZ |  |  | doors, etc. (e.g. bathrooms)
|  | ft | - height, space connected to CAZ
|  | ft3 | - volume, space connected to CAZ |  |  | Volume = length x width x height
|  | ft3 | - Total volume of CAZ and connected space |  |  | Total Volume = CAZ Volume + Connected Volume
→ |  |  | ft3 | Required Total Volume of CAZ + Connected Space
→ |  |  |  | Confined or Unconfined? Is the total volume of the CAZ plus connected
space greater or less than the volume required for combustion?
(4) If CAZ alone is confined and combustion air is provided via connection with the indoor space,
|  | y / n | - are Both connections to indoor space made within 1' of ceiling and 1' of floor?
typically, this is rectangular with a grill
|  | in | - width of opening of each connecting duct
|  | in | - length of opening of each connecting duct |  |  |  | Net Free Area Required by Code:
|  |  | - Net free area multiplier for rectangular duct (between 0 and 1) |  |  |  | ∙ interior ducts: 1 in2 for 1 kBtu/hr
|  | in2 | TOTAL cross sectional area of each duct connection |  |  |  | (but not less than 100 in2)
|  | in2 | CALCULATED cross sectional net free area required for each duct |  |  |  | minimum opening dimension is 3"
→ |  |  |  | Adequate or Undersized? Is the duct cross sectional area greater or less than the net free area required by code?

## Page 3
Visual Inspection, Equipment OFF
(1) Verify that all combustion appliances are switched OFF
| y/n | (2) Confirm the ambient CO level in the CAZ below the alarm limit (25 ppm or other ppm based on standard).
| y/n | (3) Are there any noticeable natural gas leaks?
Gas Line - inspection and leakage testing, key points
- calibrate sensor outside in clean air
- run detector at rate of 1 in/sec over all accessible gas piping
- focus attention on joints and fittings
- use soap bubbles to further verify leak locations
- note absence/presence of drip legs where gas line enters appliance
- note and recommend for replacement:
- any flexible gas connector from before 1974
- any rusted, soldered, or kinked flexible connector
- any flexible connector that enters AHU cabinet
Describe any gas leakage noted (e.g., location, suggested method of correction, etc.):
(5) CAZ - visual inspection, key points
Observe and record major "red flag" items regarding the CAZ, combustion appliances, and flue vent connections.
- CAZ Observation:
| y/n | - is the CAZ cluttered?
| y/n | - does the CAZ contain any combustable items? (e.g., stacks of newspapers, gasoline can, flammable chemicals, etc.)
Describe the CAZ, record any issues of note (e.g., leak at T&P valve, evidence of frequent relighting of pilot, combustion air openings blocked, combustibles, etc.):
- Combustion Appliances Observation:
| y/n | - verify that there is no evidence of flame rollout
| y/n | - inspect burners for soot, rust or other signs of deterioration and recommend cleaning or repair as needed
| y/n | - confirm temperature and pressure (T&P) relief lines are constructed from proper materials and that they drain properly to safe location
Describe the combustion appliances and record any issues of note (e.g., appearance, connections, common venting of two appliances, expansion tank, etc.):
- Flue Venting Observation:
| y/n | - is a draft diverter necessary and correctly installed?
| y/n | - does the flue slope upwards towards it's outside termination at a minimum of 1/4" in 12"?
| y/n | - are there obvious signs of dust, corrosion or blockage of the flue?
Describe the flue venting material and layout, and record any issues of note (e.g., appearance, proper support, slope and termination of venting, etc.):

## Page 4
Worst-Case Depressurization (WCD) of CAZ:
(1) Close all exterior doors, windows, and fireplace dampers
(2) Open all interior doors
(3) Leave open all combustion air openings to the outdoors
(4) Close doors to rooms without ducted return grilles
|  | Pa | (5) Record Base pressure in the CAZ with reference to outdoors
(6) Turn on all exhaust fans to highest setting (e.g. clothes dryers, range hoods, bathroom exhausts, etc.)
(7) Do not operate a summer (whole-house) exhaust fan
(8) Close fireplace dampers
(9) Adjust interior doors to determine worst-case depressurization in the CAZ with air handling units off
|  | Pa | (10) Record pressure in the CAZ with reference to outdoors
(11) Turn on air handling unit(s) blower(s) and repeat interior door adjustment to determine worst-case depressurization in the CAZ with blower(s) on
|  | Pa | (12) Record pressure in the CAZ with reference to outdoors
(13) Select configuration that delivers maximum Gross negative pressure in the CAZ
(use any combination of doors open/closed & AHU on/off that results in most negative pressure)
|  | Pa | (14) Record Gross pressure in the CAZ with reference to outdoors
|  | Pa | (15) Calculated NET WCD |  | Net Worst-Case Depressurization (WCD) = (Gross - Base)
→ |  |  | CAZ Risk, worst-case depressurization
CAZ WCD Relative Risk
|  | 0 to -2.9 Pa | Fairly low - indicates CAZ is reasonably disconnected from occupied space and/or minimal exhaust device impact
|  | -3 to -5 Pa | Moderate - indicates CAZ is somewhat connected to occupied space and/or impacted by exhaust devices
|  | < -5 Pa | High - indicates CAZ is reasonably connected to occupied space and/or is significantly affected by exhaust devices
Impacts of Duct Leakage
With AHU turned ON, duct leakage could affect the occupied space or CAZ
[If occupied space goes negative, so could the CAZ (if they are connected)]
| Supply leaks to unconditioned space |  |  | Occupied space is depressurized
| Return leaks from unconditioned space |  |  | Occupied space is pressurized
| Supply leaks into enclosed CAZ |  |  | CAZ is pressurized
| Return leaks from enclosed CAZ |  |  | CAZ is depressurized
Inspection and Spillage - Equipment ON:
Steps for assessing combustion appliances while in operation:
- continue to monitor CAZ ambient CO throughout appliance firing
- while under WCD, place the appliance being inspected into operation
- follow the "lighting" instructions and adjust the thermostat so appliance will operate continuously
- for furnaces: observe burners for presence of "flame dance" when the AHU blower turns on
(flame dance could indicate a heat exchanger leak)
- once burners light, confirm that electronic ignition turns off
- test for spillage at the draft hood relief opening after main burner fires
(use a mirror, smoke stick, or match flame)
|  |  | - use timer to note when spillage stops |  | Describe spillage (e.g., spillage stopped quickly - none observed after 2 minutes)
or:
- monitor spillage at 2 mins operation
- monitor spillage at 5 mins operation
- if appliance fails spillage after 5 minutes, it
should be shut off, allowed to cool (~10 min),
and then be retested under natural conditions
(all AHUs and exhaust devices off)
Analyzing combustion assessment results:
- If any combustion appliance fails the spillage test under WCD but passes under natural conditions, the cause and
potential improvement is most likely the availability of combustion air, not the vent system performance;
combustion air openings to the outdoors or other remediation to the envelope may be required.
- If the combustion appliance fails the spillage or combustion tests under natural conditions (all exhaust/AHU fans off),
the problem is likely with the appliance or the flue vent and a service technician should be consulted.

## Page 5
Measure CO in Flue: |  |  | *This test requires a probe-type combustion gas analyzer. Compare test results to table below.
| ppm | (1) After 5 min. of operation, measure undiluted CO in flue
(2) Record or calculate Air Free CO (ppm)
| ppm | - recorded Air Free CO (from instrument)
- OR
- calculate Air Free CO via either method below:
| % | - measured oxygen content (%), must be between 0-20.9
| ppm | - Air Free CO
- alternative method to calculating Air Free CO without an Oxygen meter:
| ppm | - measured CO in flue (before dilution)
| % | - measured CO2 concentration (must be < 14.1)
| LP / nat gas | - fuel type: LP or Natural gas
- fuel constant: natural gas (12.2), lp (14.0)
| ppm | - calculated Air Free CO
- If an appliance produces too much CO in the flue, a technician may need to perform a tune-up
- If another appliance is to be inspected, shut off all appliances and return to the beginning
CO Thresholds for Fossil-Fuel Fired Combustion Appliances
|  | Appliance |  | Threshold Limit
|  | Central Furnace (all categories) |  | 400 ppm air free
|  | Boiler |  | 400 ppm air free
|  | Floor Furnace |  | 400 ppm air free
|  | Gravity Furnace |  | 400 ppm air free
|  | Wall Furnace (BIV) |  | 200 ppm air free
|  | Wall Furnace (Direct Vent) |  | 400 ppm air free
|  | Vented Room Heater |  | 200 ppm air free
|  | Unvented Room Heater |  | 200 ppm air free
|  | Water Heater |  | 200 ppm air free
|  | Oven/Broiler |  | 225 ppm as measured
|  | Clothes Dryer |  | 400 ppm air free
|  | Refrigerator |  | 25 ppm as measured
|  | Gas Log (gas fireplace) |  | 25 ppm as measured in vent
|  | Gas Log (installed in wood burning fireplace) |  | 400 ppm air free in firebox
Post Testing - Return Building to Original State:
(1) Make sure equipment and thermostats are reset to their original settings
(2) Assuming no immediate safety concerns or hazards were identified during the inspection of the combustion appliances, return all appliances and systems to their pre-existing state
(3) Return doors, windows, exhaust fans, fireplace dampers, and any other fuel-gas-burning appliances to their previous condition of use
(4) If appliance-related safety concerns or hazards were identified, apply the appropriate action levels of the standard being followed (e.g., ACCA/RESNET-12 or BPI-1200)
(5) Note: In some instances the auditor may recommend that an appliance be turned off and the occupant will be advised to contact a qualified professional for further evaluation

## Conclusions from Assessment
Conclusions from Assessment:
Page 1
Page 2
Page 3
Page 4
Page 5
Recommendations

## Do Not Print
This tab is used for Excel formula formatting and is not needed for the CAZ assessment.
y
| n | LP
nat gas